Air Conditioning Commissioning Record

An air conditioning installation and commissioning record: F-gas certification, units with label scan, refrigerant type and charge, CO2 equivalent and leak check frequency, strength test, vacuum, leak test, temperatures, drains and controls, and handover.

1. System

Project

______________________________________________________________________________

Client

______________________________________________________________________________

Site *

______________________________________________________________________________

Site address

______________________________________________________________________________

Date commissioned *

______________________________________________________________________________

Time

______________________________________________________________________________

Engineer and F-gas certificate number *

______________________________________________________________________________

Company F-gas certificate number

______________________________________________________________________________

System  (choose one)

☐ Split     ☐ Multi-split     ☐ VRF or VRV     ☐ Packaged unit     ☐ Air to air heat pump

Outdoor unit make and model

______________________________________________________________________________

Scan the outdoor unit label

Scanned in the SiteSurvey app. On paper, write the numbers: serial number, model number.

______________________________________________________________________________

______________________________________________________________________________

Indoor units  (copy this block for each one)

Room *

______________________________________________________________________________

Make and model

______________________________________________________________________________

Scan the label

Scanned in the SiteSurvey app. On paper, write the numbers: serial number.

______________________________________________________________________________

2. Refrigerant

Refrigerant *  (choose one)

☐ R32     ☐ R410A     ☐ R290     ☐ R454B     ☐ Other

Global warming potential (GWP)

From the refrigerant data sheet or Annex I of the F gas Regulation, for example R32 is 675.

______________________________________________________________________________

Factory charge (kg)

______________________________________________________________________________

Additional charge (kg)

______________________________________________________________________________

Total charge (kg)  (if applicable; worked out automatically in the app)

______________________________________________________________________________

Tonnes CO2 equivalent  (if applicable; worked out automatically in the app)

______________________________________________________________________________

Great Britain F gas rules (retained Regulation (EU) No 517/2014, article 4): leak checks depend on the charge in tonnes of CO2 equivalent, which is the charge in kg times the GWP, divided by 1,000.

If applicable: Under 5 tonnes CO2 equivalent: the F gas rules do not require leak checks.

If applicable: 5 to under 50 tonnes CO2 equivalent: leak check at least every 12 months, or every 24 months with a leak detection system. Equipment labelled as hermetically sealed and under 10 tonnes is exempt. Keep F gas records for 5 years.

If applicable: 50 to under 500 tonnes CO2 equivalent: leak check at least every 6 months, or every 12 months with a leak detection system. Keep F gas records for 5 years.

If applicable: 500 tonnes CO2 equivalent or more: a leak detection system must be fitted, and leak checks are needed at least every 6 months with it (every 3 months without). Keep F gas records for 5 years.

3. Tests

Nitrogen strength test (bar)

______________________________________________________________________________

Held for (minutes)

______________________________________________________________________________

Pressure held?

☐ Yes     ☐ No

Vacuum achieved (microns)

______________________________________________________________________________

Leak test passed?

☐ Yes     ☐ No

Return air temperature (°C)

______________________________________________________________________________

Supply air temperature (°C)

______________________________________________________________________________

Air temperature difference (°C)  (if applicable; worked out automatically in the app)

______________________________________________________________________________

Condensate drains tested?

☐ Yes     ☐ No

Controls set up and shown to the customer?

☐ Yes     ☐ No

Unit labelled with refrigerant type and charge?

☐ Yes     ☐ No

Photos of the units, pipework and labels  (photos: attach, or note the file names)

______________________________________________________________________________

4. Handover

Customer name

______________________________________________________________________________

Customer signature

Completed by *

______________________________________________________________________________

Signature