Commercial Catering Gas Check

A commercial kitchen gas safety site record: each appliance checked, gas tightness, ventilation and the gas interlock, flues and flame supervision, emergency isolation, unsafe situations and the engineer's sign-off.

1. Kitchen

Project

______________________________________________________________________________

Client

______________________________________________________________________________

Site *

______________________________________________________________________________

Site address

______________________________________________________________________________

Date *

______________________________________________________________________________

Time

______________________________________________________________________________

Engineer *

______________________________________________________________________________

Gas Safe registration number *

______________________________________________________________________________

Does the engineer hold the commercial catering gas competence?

☐ Yes     ☐ No

If applicable: HSE CAIS23: gas work must be done by a Gas Safe registered business whose engineers hold valid certificates of competence for the types of gas equipment and work involved. Check the engineer's Gas Safe ID card.

This is a site record of the checks. Issue your formal gas safety certificate or report from your own software.

2. Gas supply, ventilation and interlock

Gas tightness test *  (choose one)

☐ Pass     ☐ Fail

Emergency isolation valve accessible and labelled  (choose one)

☐ OK     ☐ Defect

Mechanical ventilation working  (choose one)

☐ OK     ☐ Defect     ☐ Natural ventilation only

Gas interlock shuts off the gas if the ventilation fails  (choose one)

☐ OK     ☐ Defect     ☐ Not fitted

If applicable: HSE CAIS23: where there is mechanical ventilation, an interlock should shut off the gas supply to the appliances if the ventilation fails, and manual bypasses are not permitted. BS 6173 is not retrospective: where there is no interlock, assess the risk and make sure it is prevented or controlled.

CO2 level in the kitchen (ppm), if measured

______________________________________________________________________________

3. Appliances

Appliances  (copy this block for each one)

Appliance (for example 6-burner range, fryer, combi oven) *

______________________________________________________________________________

Scan the data plate

Scanned in the SiteSurvey app. On paper, write the numbers: serial number, model number.

______________________________________________________________________________

______________________________________________________________________________

Flame supervision devices work  (choose one)

☐ OK     ☐ Defect     ☐ Not fitted

Flue or extract canopy  (choose one)

☐ OK     ☐ Defect

Combustion and burner pressure  (choose one)

☐ OK     ☐ Defect

Result *  (choose one)

☐ Safe     ☐ At risk     ☐ Immediately dangerous

Action taken  (if applicable)

______________________________________________________________________________

If applicable: At risk (IGEM/G/11): explain the risk and, with the responsible person's permission, turn off the gas supply to the appliance and attach a DANGER DO NOT USE label.

If applicable: Immediately dangerous (IGEM/G/11): with the responsible person's permission, disconnect and seal the gas supply and attach a DANGER DO NOT USE label.

Warning notice given to the responsible person and signed?  (if applicable)

☐ Yes     ☐ No

Photos  (photos: attach, or note the file names)

______________________________________________________________________________

Appliances at risk  (worked out automatically in the app)

______________________________________________________________________________

Appliances immediately dangerous  (worked out automatically in the app)

______________________________________________________________________________

Next check due

HSE CAIS23: follow the manufacturer's recommendations, but as a general rule annual inspections are a reasonable minimum.

______________________________________________________________________________

If applicable: The next check date is before the date of this check.

4. Sign-off

Kitchen manager name

______________________________________________________________________________

Kitchen manager signature

Completed by *

______________________________________________________________________________

Signature