Dry Riser Inspection Record

A dry riser inspection and test record: building and check type, inlet box, each outlet's valve, cap, strap and signage, the annual pressure test, faults, and the 24-hour reporting rule for high-rise residential buildings.

1. Building

Project

______________________________________________________________________________

Client

______________________________________________________________________________

Site *

______________________________________________________________________________

Site address

______________________________________________________________________________

Date *

______________________________________________________________________________

Time

______________________________________________________________________________

Engineer or checker *

______________________________________________________________________________

Check *  (choose one)

☐ Monthly routine check     ☐ Six-monthly visual inspection     ☐ Annual pressure test

Storeys

______________________________________________________________________________

Does the building have two or more homes and is it at least 18 m high or 7 storeys?

☐ Yes     ☐ No

If applicable: Fire Safety (England) Regulations 2022, regulation 7: in a high-rise residential building the responsible person must carry out monthly routine checks of essential fire-fighting equipment, which includes dry riser inlets and outlets, and keep a record that residents can see. If a fault cannot be fixed within 24 hours, it must be reported to the fire and rescue service electronically, and reported again when fixed.

BAFSA guidance on rising mains to BS 9990: check dry risers every six months and carry out a wet pressure test every year. Article 38 of the Fire Safety Order requires equipment provided for fire-fighters to be maintained in efficient working order and good repair.

2. Inlet

Inlet location

______________________________________________________________________________

Inlet box, door and glass  (choose one)

☐ OK     ☐ Defect

What is wrong?  (if applicable)

______________________________________________________________________________

Dry riser inlet sign  (choose one)

☐ OK     ☐ Defect

What is wrong?  (if applicable)

______________________________________________________________________________

Inlet valves and caps  (choose one)

☐ OK     ☐ Defect

What is wrong?  (if applicable)

______________________________________________________________________________

Drain valve closed  (choose one)

☐ OK     ☐ Defect

What is wrong?  (if applicable)

______________________________________________________________________________

Clear access for the fire service  (choose one)

☐ OK     ☐ Defect

What is wrong?  (if applicable)

______________________________________________________________________________

Photos of the inlet  (photos: attach, or note the file names)

______________________________________________________________________________

3. Outlets

Outlets  (copy this block for each one)

Floor *

______________________________________________________________________________

Landing valve closed, strapped and padlocked  (choose one)

☐ OK     ☐ Defect

Blank cap and chain  (choose one)

☐ OK     ☐ Defect

Outlet box and sign  (choose one)

☐ OK     ☐ Defect

What is wrong?  (if applicable)

______________________________________________________________________________

4. Pressure test and result

Test pressure (bar)  (if applicable)

______________________________________________________________________________

Held for (minutes)  (if applicable)

______________________________________________________________________________

Pressure held with no leaks?  (if applicable)

☐ Yes     ☐ No

Result *  (choose one)

☐ In efficient working order     ☐ Faults found

Faults and action  (if applicable)

______________________________________________________________________________

______________________________________________________________________________

______________________________________________________________________________

Will the faults be fixed within 24 hours?  (if applicable)

☐ Yes     ☐ No

If applicable: Report the fault to the fire and rescue service electronically, and report again when it is fixed.

Date reported to the fire and rescue service  (if applicable)

______________________________________________________________________________

Report reference  (if applicable)

______________________________________________________________________________

Completed by *

______________________________________________________________________________

Signature