Electrical Installation Record

A site record for new electrical work that needs an Electrical Installation Certificate: scope, supply and earthing, bonding, each new circuit with its tests, inspection items, departures and the three sign-offs.

1. Work

Project

______________________________________________________________________________

Client

______________________________________________________________________________

Site *

______________________________________________________________________________

Site address

______________________________________________________________________________

Date completed *

______________________________________________________________________________

Time

______________________________________________________________________________

Contractor and registration scheme number *

______________________________________________________________________________

Type of work *  (choose one)

☐ New installation

☐ Rewire

☐ Addition with one or more new circuits

☐ Consumer unit replacement

☐ Alteration

Extent of the work covered *

______________________________________________________________________________

______________________________________________________________________________

______________________________________________________________________________

The notes on the IET model Electrical Installation Certificate say it is used for a new installation, for an addition or alteration that introduces one or more new circuits, and for replacing a consumer unit or distribution board. An addition or alteration that does not introduce a new circuit may go on a Minor Electrical Installation Works Certificate.

Is the work in a dwelling in England?

☐ Yes     ☐ No

If applicable: Approved Document P: in a dwelling, installing a new circuit, replacing a consumer unit, or any addition or alteration to existing circuits in a special location (such as the space around a bath or shower) is notifiable. It must be certified by a registered competent person, a registered third-party certifier or a building control body.

This is a site record of the work and test results, not the certificate itself. The formal certificate and its schedules are issued from the registration scheme's or certification software.

2. Supply and earthing

Earthing arrangement *  (choose one)

☐ TN-C-S (PME)     ☐ TN-S     ☐ TT

Supply  (choose one)

☐ Single-phase     ☐ Three-phase

External earth fault loop impedance Ze (Ω)

______________________________________________________________________________

Prospective fault current (kA)

______________________________________________________________________________

Main switch rating (A)

______________________________________________________________________________

Main earthing conductor size (mm²)

______________________________________________________________________________

Earth electrode resistance (Ω)  (if applicable)

______________________________________________________________________________

Main protective bonding connected to  (tick all that apply)

☐ Water

☐ Gas

☐ Oil

☐ Structural steel

☐ Lightning protection

☐ Other: ____________

☐ None present

Distribution board or consumer unit

______________________________________________________________________________

Scan the board label

Scanned in the SiteSurvey app. On paper, write the numbers: serial number, model number.

______________________________________________________________________________

______________________________________________________________________________

Photos of the board and labelling  (photos: attach, or note the file names)

______________________________________________________________________________

3. Circuits and tests

Circuits  (copy this block for each one)

Circuit number *

______________________________________________________________________________

Description

______________________________________________________________________________

Protective device  (choose one)

☐ MCB type B

☐ MCB type C

☐ MCB type D

☐ RCBO type B

☐ RCBO type C

☐ BS 88 fuse

☐ BS 1361 fuse

☐ BS 3036 rewireable fuse

☐ Other

Rating (A)

______________________________________________________________________________

RCD type  (choose one)

☐ Type AC     ☐ Type A     ☐ Type F     ☐ Type B     ☐ No RCD

Live conductor (mm²)

______________________________________________________________________________

Protective conductor (mm²)

______________________________________________________________________________

Continuity R1 + R2 (Ω)

______________________________________________________________________________

Insulation resistance test voltage  (choose one)

☐ 250 V     ☐ 500 V     ☐ 1000 V

Insulation resistance, live to live (MΩ)

______________________________________________________________________________

Insulation resistance, live to earth (MΩ)

______________________________________________________________________________

If applicable: Below 1 MΩ. The IET gives 1 MΩ as the minimum insulation resistance, with a 500 V d.c. test for circuits up to 500 V. Investigate before the circuit is put into service.

Polarity  (choose one)

☐ Correct     ☐ Fault

Earth fault loop impedance Zs, measured (Ω)

______________________________________________________________________________

Maximum permitted Zs for this device (Ω)

From the BS 7671 tables or the device manufacturer.

______________________________________________________________________________

If applicable: Measured Zs is above the maximum permitted for this protective device. The device may not disconnect in time.

RCD operating time at rated residual current (ms)

______________________________________________________________________________

If applicable: Over 300 ms at the rated residual current. IET guidance gives 300 ms as the maximum for a general non-delay RCD (an S type time-delayed RCD may take up to 500 ms). Check or replace the RCD.

Result *  (choose one)

☐ Pass     ☐ Fail

What failed and what was done  (if applicable)

______________________________________________________________________________

______________________________________________________________________________

______________________________________________________________________________

Circuits failed  (worked out automatically in the app)

______________________________________________________________________________

Circuits passed  (worked out automatically in the app)

______________________________________________________________________________

4. Inspection and departures

Inspected and correct *  (tick all that apply)

☐ Cables selected and installed correctly

☐ Protective devices suit the circuits

☐ Isolation and switching

☐ Fire barriers and sealing

☐ Labels and warning notices

☐ Surge protection considered

☐ Additional protection by RCD where required

Comments on the existing installation  (if applicable)

Defects seen in the existing installation that this work does not cover.

______________________________________________________________________________

______________________________________________________________________________

______________________________________________________________________________

Are there any departures from BS 7671?

☐ Yes     ☐ No

Departures and why they are acceptable  (if applicable)

______________________________________________________________________________

______________________________________________________________________________

______________________________________________________________________________

Recommended date of next inspection

______________________________________________________________________________

5. Sign-off

Did one person do the design, construction and inspection and testing?

☐ Yes     ☐ No

Design: name *

If one person did the design, construction and inspection and testing, they sign here for all three.

______________________________________________________________________________

Design: signature

Construction: name  (if applicable)

______________________________________________________________________________

Construction: signature  (if applicable)

Inspection and testing: name  (if applicable)

______________________________________________________________________________

Inspection and testing: signature  (if applicable)

Client name

______________________________________________________________________________

Client signature