Electrical Installation Record
A site record for new electrical work that needs an Electrical Installation Certificate: scope, supply and earthing, bonding, each new circuit with its tests, inspection items, departures and the three sign-offs.
1. Work
Project
______________________________________________________________________________
Client
______________________________________________________________________________
Site *
______________________________________________________________________________
Site address
______________________________________________________________________________
Date completed *
______________________________________________________________________________
Time
______________________________________________________________________________
Contractor and registration scheme number *
______________________________________________________________________________
Type of work *  (choose one)
☐ New installation
☐ Rewire
☐ Addition with one or more new circuits
☐ Consumer unit replacement
☐ Alteration
Extent of the work covered *
______________________________________________________________________________
______________________________________________________________________________
______________________________________________________________________________
	The notes on the IET model Electrical Installation Certificate say it is used for a new installation, for an addition or alteration that introduces one or more new circuits, and for replacing a consumer unit or distribution board. An addition or alteration that does not introduce a new circuit may go on a Minor Electrical Installation Works Certificate.



Is the work in a dwelling in England?
☐ Yes     ☐ No
	If applicable: Approved Document P: in a dwelling, installing a new circuit, replacing a consumer unit, or any addition or alteration to existing circuits in a special location (such as the space around a bath or shower) is notifiable. It must be certified by a registered competent person, a registered third-party certifier or a building control body.



	This is a site record of the work and test results, not the certificate itself. The formal certificate and its schedules are issued from the registration scheme's or certification software.



2. Supply and earthing
Earthing arrangement *  (choose one)
☐ TN-C-S (PME)     ☐ TN-S     ☐ TT
Supply  (choose one)
☐ Single-phase     ☐ Three-phase
External earth fault loop impedance Ze (Ω)
______________________________________________________________________________
Prospective fault current (kA)
______________________________________________________________________________
Main switch rating (A)
______________________________________________________________________________
Main earthing conductor size (mm²)
______________________________________________________________________________
Earth electrode resistance (Ω)  (if applicable)
______________________________________________________________________________
Main protective bonding connected to  (tick all that apply)
☐ Water
☐ Gas
☐ Oil
☐ Structural steel
☐ Lightning protection
☐ Other: ____________
☐ None present
Distribution board or consumer unit
______________________________________________________________________________
Scan the board label
Scanned in the SiteSurvey app. On paper, write the numbers: serial number, model number.
______________________________________________________________________________
______________________________________________________________________________
Photos of the board and labelling  (photos: attach, or note the file names)
______________________________________________________________________________
3. Circuits and tests
Circuits  (copy this block for each one)
Circuit number *
______________________________________________________________________________
Description
______________________________________________________________________________
Protective device  (choose one)
☐ MCB type B
☐ MCB type C
☐ MCB type D
☐ RCBO type B
☐ RCBO type C
☐ BS 88 fuse
☐ BS 1361 fuse
☐ BS 3036 rewireable fuse
☐ Other
Rating (A)
______________________________________________________________________________
RCD type  (choose one)
☐ Type AC     ☐ Type A     ☐ Type F     ☐ Type B     ☐ No RCD
Live conductor (mm²)
______________________________________________________________________________
Protective conductor (mm²)
______________________________________________________________________________
Continuity R1 + R2 (Ω)
______________________________________________________________________________
Insulation resistance test voltage  (choose one)
☐ 250 V     ☐ 500 V     ☐ 1000 V
Insulation resistance, live to live (MΩ)
______________________________________________________________________________
Insulation resistance, live to earth (MΩ)
______________________________________________________________________________
	If applicable: Below 1 MΩ. The IET gives 1 MΩ as the minimum insulation resistance, with a 500 V d.c. test for circuits up to 500 V. Investigate before the circuit is put into service.



Polarity  (choose one)
☐ Correct     ☐ Fault
Earth fault loop impedance Zs, measured (Ω)
______________________________________________________________________________
Maximum permitted Zs for this device (Ω)
From the BS 7671 tables or the device manufacturer.
______________________________________________________________________________
	If applicable: Measured Zs is above the maximum permitted for this protective device. The device may not disconnect in time.



RCD operating time at rated residual current (ms)
______________________________________________________________________________
	If applicable: Over 300 ms at the rated residual current. IET guidance gives 300 ms as the maximum for a general non-delay RCD (an S type time-delayed RCD may take up to 500 ms). Check or replace the RCD.



Result *  (choose one)
☐ Pass     ☐ Fail
What failed and what was done  (if applicable)
______________________________________________________________________________
______________________________________________________________________________
______________________________________________________________________________
Circuits failed  (worked out automatically in the app)
______________________________________________________________________________
Circuits passed  (worked out automatically in the app)
______________________________________________________________________________
4. Inspection and departures
Inspected and correct *  (tick all that apply)
☐ Cables selected and installed correctly
☐ Protective devices suit the circuits
☐ Isolation and switching
☐ Fire barriers and sealing
☐ Labels and warning notices
☐ Surge protection considered
☐ Additional protection by RCD where required
Comments on the existing installation  (if applicable)
Defects seen in the existing installation that this work does not cover.
______________________________________________________________________________
______________________________________________________________________________
______________________________________________________________________________
Are there any departures from BS 7671?
☐ Yes     ☐ No
Departures and why they are acceptable  (if applicable)
______________________________________________________________________________
______________________________________________________________________________
______________________________________________________________________________
Recommended date of next inspection
______________________________________________________________________________
5. Sign-off
Did one person do the design, construction and inspection and testing?
☐ Yes     ☐ No
Design: name *
If one person did the design, construction and inspection and testing, they sign here for all three.
______________________________________________________________________________
Design: signature
	



Construction: name  (if applicable)
______________________________________________________________________________
Construction: signature  (if applicable)
	



Inspection and testing: name  (if applicable)
______________________________________________________________________________
Inspection and testing: signature  (if applicable)
	



Client name
______________________________________________________________________________
Client signature
	



Electrical Installation Record. Printable copy from the SiteSurvey form library. Fill it in on a phone, with photos and signatures: sitesurvey.app/forms/electrical-installation-certificate-template/




