Electrical Minor Works Record

An electrical minor works site record: the work done, the circuit it was on, earthing and protection, continuity, insulation resistance, polarity, Zs and RCD tests, departures and Part P notification.

1. Work done

Project

______________________________________________________________________________

Client

______________________________________________________________________________

Site *

______________________________________________________________________________

Site address

______________________________________________________________________________

Date the work was completed *

______________________________________________________________________________

Time

______________________________________________________________________________

Electrician *

______________________________________________________________________________

Registration scheme and number

______________________________________________________________________________

Description of the minor works *

______________________________________________________________________________

______________________________________________________________________________

______________________________________________________________________________

Location of the work

______________________________________________________________________________

A minor works certificate is for additions or alterations to an existing circuit that do not add a new circuit, such as an extra socket or light, or moving a switch. A new circuit or a consumer unit replacement needs an Electrical Installation Certificate.

This is a site record of the readings and checks. It is not the BS 7671 certificate or schedule itself: issue that from your registration scheme's or your certification software.

2. Circuit and protection

Distribution board and circuit number *

______________________________________________________________________________

Earthing arrangement  (choose one)

☐ TN-C-S (PME)     ☐ TN-S     ☐ TT     ☐ Other

Earth fault loop impedance at the distribution board, Zdb (Ω)

______________________________________________________________________________

Earthing conductor and main protective bonding present and adequate?

☐ Yes     ☐ No

Protective device  (choose one)

☐ MCB type B

☐ MCB type C

☐ MCB type D

☐ RCBO type B

☐ RCBO type C

☐ BS 88 fuse

☐ BS 1361 fuse

☐ BS 3036 rewireable fuse

☐ Other

Rating (A)

______________________________________________________________________________

RCD type  (choose one)

☐ Type AC     ☐ Type A     ☐ Type F     ☐ Type B     ☐ No RCD

RCD rated residual current (mA)

______________________________________________________________________________

Arc fault detection device fitted?

☐ Yes     ☐ No

Departures from BS 7671, if any

______________________________________________________________________________

______________________________________________________________________________

______________________________________________________________________________

3. Tests

Protective conductor continuity R1 + R2 or R2 (Ω)

______________________________________________________________________________

Insulation resistance test voltage  (choose one)

☐ 250 V     ☐ 500 V     ☐ 1000 V

Insulation resistance, live to live (MΩ)

______________________________________________________________________________

Insulation resistance, live to earth (MΩ)

______________________________________________________________________________

If applicable: Below 1 MΩ. The IET gives 1 MΩ as the minimum insulation resistance, with a 500 V d.c. test for circuits up to 500 V. Investigate before the circuit is put into service.

Polarity  (choose one)

☐ Correct     ☐ Fault

Earth fault loop impedance Zs, measured (Ω)

______________________________________________________________________________

Maximum permitted Zs for this device (Ω)

From the BS 7671 tables or the device manufacturer.

______________________________________________________________________________

If applicable: Measured Zs is above the maximum permitted for this protective device. The device may not disconnect in time.

RCD operating time at rated residual current (ms)

______________________________________________________________________________

If applicable: Over 300 ms at the rated residual current. IET guidance gives 300 ms as the maximum for a general non-delay RCD (an S type time-delayed RCD may take up to 500 ms). Check or replace the RCD.

RCD test button operates  (choose one)

☐ Yes     ☐ No     ☐ No RCD

AFDD test button operates  (choose one)

☐ Yes     ☐ No     ☐ Not fitted

Comments on the existing installation

______________________________________________________________________________

______________________________________________________________________________

______________________________________________________________________________

Is the work notifiable under Part P of the Building Regulations (England)?

Notifiable: a new circuit, a consumer unit replacement, or any addition or alteration to an existing circuit in a special location (the space around a bath or shower, or a room with a swimming pool or sauna heater).

☐ Yes     ☐ No

If applicable: Notifiable work must be self-certified by a registered competent person, certified by a registered third-party certifier appointed before work starts, or notified to a building control body before work starts (Approved Document P).

Name *

______________________________________________________________________________

Signature