Electrical Test Results Schedule
An electrical test results schedule for a distribution board: every circuit with its device, cables, continuity, insulation resistance, polarity, Zs and RCD times, with warnings on readings that fail.
1. Board and supply
Project
______________________________________________________________________________
Client
______________________________________________________________________________
Site *
______________________________________________________________________________
Site address
______________________________________________________________________________
Date of the tests *
______________________________________________________________________________
Time
______________________________________________________________________________
Tested by *
______________________________________________________________________________
Distribution board reference and location *
______________________________________________________________________________
Scan the board label
Scanned in the SiteSurvey app. On paper, write the numbers: asset number.
______________________________________________________________________________
Photos of the board  (photos: attach, or note the file names)
Optional. The board with its cover on and off, the circuit chart and anything you found.
______________________________________________________________________________
Earthing arrangement  (choose one)
☐ TN-C-S (PME)     ☐ TN-S     ☐ TT     ☐ Other
Earth fault loop impedance at the board, Ze or Zdb (Ω)
Ze at the origin, or Zdb at a sub-distribution board.
______________________________________________________________________________
Prospective fault current (kA)
______________________________________________________________________________
Test instrument, serial number and calibration date
______________________________________________________________________________
	This is a site record of the readings and checks. It is not the BS 7671 certificate or schedule itself: issue that from your registration scheme's or your certification software.



2. Circuits
Circuits tested  (copy this block for each one)
Circuit number *
______________________________________________________________________________
Circuit description *
______________________________________________________________________________
Points served
______________________________________________________________________________
Live conductor (mm²)
______________________________________________________________________________
Protective conductor (mm²)
______________________________________________________________________________
Protective device  (choose one)
☐ MCB type B
☐ MCB type C
☐ MCB type D
☐ RCBO type B
☐ RCBO type C
☐ BS 88 fuse
☐ BS 1361 fuse
☐ BS 3036 rewireable fuse
☐ Other
Rating (A)
______________________________________________________________________________
RCD type  (choose one)
☐ Type AC     ☐ Type A     ☐ Type F     ☐ Type B     ☐ No RCD
Ring final circuit?
☐ Yes     ☐ No
Ring end to end r1 (Ω)  (if applicable)
______________________________________________________________________________
Ring end to end rn (Ω)  (if applicable)
______________________________________________________________________________
Ring end to end r2 (Ω)  (if applicable)
______________________________________________________________________________
Difference between r1 and rn (Ω)  (if applicable; worked out automatically in the app)
______________________________________________________________________________
(r1 + r2) / 4, the expected R1 + R2 for the ring (Ω)  (if applicable; worked out automatically in the app)
______________________________________________________________________________
Continuity R1 + R2 (Ω)
______________________________________________________________________________
Ze + (R1 + R2) (Ω)  (if applicable; worked out automatically in the app)
Ze or Zdb from page 1 plus R1 + R2. Compare it with the measured Zs below.
______________________________________________________________________________
Insulation resistance test voltage  (choose one)
☐ 250 V     ☐ 500 V     ☐ 1000 V
Insulation resistance, live to live (MΩ)
______________________________________________________________________________
Insulation resistance, live to earth (MΩ)
______________________________________________________________________________
	If applicable: Below 1 MΩ. The IET gives 1 MΩ as the minimum insulation resistance, with a 500 V d.c. test for circuits up to 500 V. Investigate before the circuit is put into service.



Polarity  (choose one)
☐ Correct     ☐ Fault
Earth fault loop impedance Zs, measured (Ω)
______________________________________________________________________________
Maximum permitted Zs for this device (Ω)
From the BS 7671 tables or the device manufacturer.
______________________________________________________________________________
Measured Zs as a share of the maximum (%)  (if applicable; worked out automatically in the app)
______________________________________________________________________________
	If applicable: Measured Zs is above the maximum permitted for this protective device. The device may not disconnect in time.



RCD operating time at rated residual current (ms)
______________________________________________________________________________
	If applicable: Over 300 ms at the rated residual current. IET guidance gives 300 ms as the maximum for a general non-delay RCD (an S type time-delayed RCD may take up to 500 ms). Check or replace the RCD.



RCD or AFDD test button operates  (choose one)
☐ Yes     ☐ No     ☐ Not fitted
Result *  (choose one)
☐ Pass     ☐ Fail
	If applicable: Recorded as a pass, but a reading above is outside a limit the form checks. Check the reading and the result.



Observations  (if applicable)
______________________________________________________________________________
______________________________________________________________________________
______________________________________________________________________________
c_f_pass  (worked out automatically in the app)
______________________________________________________________________________
c_f_fail  (worked out automatically in the app)
______________________________________________________________________________
c_f_ir  (worked out automatically in the app)
______________________________________________________________________________
c_f_zs  (worked out automatically in the app)
______________________________________________________________________________
c_f_rcd  (worked out automatically in the app)
______________________________________________________________________________
Circuit retest readings  (copy this block for each one)
	One row per retest of this circuit. Record only the tests performed, with the test conditions and acceptance reference in the notes. The original circuit schedule and its calculations remain above.



Reading date and time *
______________________________________________________________________________
Continuity R1 + R2 (Ω)
______________________________________________________________________________
Insulation test voltage (V)  (choose one)
☐ 250     ☐ 500     ☐ 1000
Insulation resistance: live to earth (MΩ)
______________________________________________________________________________
Earth fault loop impedance Zs (Ω)
______________________________________________________________________________
RCD operating time (ms)
______________________________________________________________________________
Recorded result  (choose one)
☐ Not assessed     ☐ Pass     ☐ Fail     ☐ Not tested
Notes / action taken
______________________________________________________________________________
______________________________________________________________________________
______________________________________________________________________________
Photos for this reading  (photos: attach, or note the file names)
______________________________________________________________________________
Circuits tested  (worked out automatically in the app)
______________________________________________________________________________
Circuits passed  (worked out automatically in the app)
______________________________________________________________________________
Circuits failed  (worked out automatically in the app)
______________________________________________________________________________
Insulation under 1 MΩ at 500 V  (worked out automatically in the app)
______________________________________________________________________________
Zs over the maximum  (worked out automatically in the app)
______________________________________________________________________________
RCD slower than 300 ms  (worked out automatically in the app)
______________________________________________________________________________
Highest Zs as a share of its maximum (%)  (if applicable; worked out automatically in the app)
______________________________________________________________________________
3. Actions and sign-off
Are further actions needed?
☐ Yes     ☐ No
	If applicable: A circuit failed, but no further action is recorded. Add what needs doing, who will do it and when.



Further actions  (copy this block for each one; if applicable)
What needs doing? *
______________________________________________________________________________
______________________________________________________________________________
______________________________________________________________________________
Who will do it?
______________________________________________________________________________
Due date
______________________________________________________________________________
Status  (choose one)
☐ Open     ☐ In progress     ☐ Completed
Inspector name *
______________________________________________________________________________
Position or company
______________________________________________________________________________
Inspector signature
	



	Signing records what was found on the day. It does not make unsafe equipment safe or replace a thorough examination, design check or service by a competent person.



Electrical Test Results Schedule. Printable copy from the SiteSurvey form library. Fill it in on a phone, with photos and signatures: sitesurvey.app/forms/schedule-of-test-results-template/




