Fire Damper Test Record

A fire damper drop test record: each damper with its location, type and access, visual check, drop test, reset, result and photos, with failed dampers counted and the annual testing guidance.

1. Visit

Project

______________________________________________________________________________

Client

______________________________________________________________________________

Site *

______________________________________________________________________________

Site address

______________________________________________________________________________

Test date *

______________________________________________________________________________

Time

______________________________________________________________________________

Engineer *

______________________________________________________________________________

Damper schedule or drawing reference

______________________________________________________________________________

BESA guidance on BS 9999: fire dampers should be tested by a competent person on completion of installation and at least annually after that, more often in dusty or polluted air. The Fire Safety Order (article 17) requires fire safety equipment to be maintained in efficient working order and in good repair.

2. Dampers

Dampers  (copy this block for each one)

Damper reference *

______________________________________________________________________________

Scan the damper label

Scanned in the SiteSurvey app. On paper, write the numbers: damper id, serial number.

______________________________________________________________________________

______________________________________________________________________________

Location

______________________________________________________________________________

Type  (choose one)

☐ Fusible link (spring)     ☐ Motorised fire damper     ☐ Fire and smoke damper

Access panel available?

☐ Yes     ☐ No

Visual check (clean, no corrosion, no obstruction)  (if applicable; choose one)

☐ OK     ☐ Defect

Drop test: closed fully  (if applicable; choose one)

☐ Pass     ☐ Fail

Reset and left open?  (if applicable)

☐ Yes     ☐ No

Fusible link replaced with a correctly rated link?  (if applicable)

☐ Yes     ☐ No

Result *  (choose one)

☐ Pass     ☐ Fail     ☐ No access

Fault and action  (if applicable)

______________________________________________________________________________

Photos (before and after the test)  (photos: attach, or note the file names)

______________________________________________________________________________

Dampers passed  (worked out automatically in the app)

______________________________________________________________________________

Dampers failed  (worked out automatically in the app)

______________________________________________________________________________

Dampers with no access  (worked out automatically in the app)

______________________________________________________________________________

If applicable: A failed damper may not close in a fire. Arrange repair or replacement and tell the responsible person.

Who will arrange the remedial work, and by when?  (if applicable)

______________________________________________________________________________

Next test due

______________________________________________________________________________

3. Sign-off

Responsible person or site contact name

______________________________________________________________________________

Responsible person or site contact signature

Completed by *

______________________________________________________________________________

Signature