Hot Tub and Spa Pool Check
A hot tub and spa pool check to HSE HSG282: water clarity, pH and disinfectant tests with HSG282 action limits, jets, overflows, grilles and filter, cover, steps and cabinet, cleaning done, open or closed, and sign-off.
1. Hot tub
Project
______________________________________________________________________________
Client
______________________________________________________________________________
Site *
______________________________________________________________________________
Site address
______________________________________________________________________________
Check date *
______________________________________________________________________________
Time
______________________________________________________________________________
Checked by *
______________________________________________________________________________
Hot tub or spa pool (unit or location) *
______________________________________________________________________________
Setting  (choose one)
☐ Holiday park or lodge
☐ Hotel room
☐ Hotel or leisure spa
☐ Gym or club
☐ Showroom or display
☐ Other
Type  (choose one)
☐ Domestic-type hot tub     ☐ Commercial-type spa pool
Check  (choose one)
☐ Routine water test
☐ Between lettings (drain, clean and refill)
☐ Weekly check
☐ Monthly check
State  (choose one)
☐ In use     ☐ Not in use
Is the written control scheme (normal operating plan) on site?
☐ Yes     ☐ No
	HSE HSG282 covers the control of legionella and other infectious agents in spa pools. Domestic-type hot tubs used as part of a business, for example in a holiday park rental unit or a hotel bedroom, are subject to the general duties of the Health and Safety at Work etc. Act 1974. HSG282 says records of monitoring, inspections, tests and checks should be kept for at least five years, and should show who did the work and when.



2. Water tests
	HSG282 Table 1, domestic-type hot tubs: check water clarity, pH and disinfectant at least twice a day depending on the risk assessment and use; drain, clean the whole system and refill between each group of users or at least weekly, whichever is shorter. For commercial-type spa pools, test at opening and every two hours. Follow your own risk assessment.



Water tests  (copy this block for each one)
Time *
______________________________________________________________________________
Water clarity  (choose one)
☐ Clear     ☐ Cloudy
pH
______________________________________________________________________________
Disinfectant  (choose one)
☐ Chlorine     ☐ Bromine
Free chlorine or total active bromine (mg/l)
______________________________________________________________________________
Combined chlorine (mg/l)  (if applicable)
______________________________________________________________________________
	If applicable: pH outside 7.0 to 7.6. HSG282 Table 3: close the spa pool and check the operation and calibration of the dosing units, then recheck.



	If applicable: Disinfectant outside the HSG282 Table 3 limits (chlorine below 1 or above 10 mg/l, bromine below 2 or above 12 mg/l): close the spa pool, apply corrective actions and retest.



	If applicable: Disinfectant outside the typical range (chlorine 3 to 5 mg/l, bromine 4 to 6 mg/l). HSG282 Table 3: check the dosing units are operating correctly.



	If applicable: Combined chlorine above 1 mg/l. HSG282 Table 3: review the control measures.



Action taken  (if applicable; choose one)
☐ Closed until corrected     ☐ Corrected and retested
Dosing system working  (choose one)
☐ OK     ☐ Defect     ☐ Not fitted
Microbiological sample taken today?
☐ Yes     ☐ No
Sample reference and laboratory  (if applicable)
______________________________________________________________________________
	If applicable: HSG282 Table 1 typical frequency: microbiological testing monthly (aerobic colony count, coliforms, E. coli, P. aeruginosa) and quarterly for legionella.



3. Condition
	HSG282 says the review of a spa pool should include inspecting the accessible parts for damage and signs of contamination, such as biofilms, and the condition of the jets, overflows and grilles.



Water line clean  (choose one)
☐ OK     ☐ Defect     ☐ Not applicable
What is wrong?  (if applicable)
______________________________________________________________________________
Overflow channels and skimmer clean  (choose one)
☐ OK     ☐ Defect     ☐ Not applicable
What is wrong?  (if applicable)
______________________________________________________________________________
Jets: no damage, blockage or biofilm  (choose one)
☐ OK     ☐ Defect     ☐ Not applicable
What is wrong?  (if applicable)
______________________________________________________________________________
Suction grilles and strainers in place and undamaged  (choose one)
☐ OK     ☐ Defect     ☐ Not applicable
What is wrong?  (if applicable)
______________________________________________________________________________
Filter cartridge clean  (choose one)
☐ OK     ☐ Defect     ☐ Not applicable
What is wrong?  (if applicable)
______________________________________________________________________________
Cover, straps and locks secure  (choose one)
☐ OK     ☐ Defect     ☐ Not applicable
What is wrong?  (if applicable)
______________________________________________________________________________
Steps and surround: no damage or slip hazard  (choose one)
☐ OK     ☐ Defect     ☐ Not applicable
What is wrong?  (if applicable)
______________________________________________________________________________
Equipment cabinet closed and secure  (choose one)
☐ OK     ☐ Defect     ☐ Not applicable
What is wrong?  (if applicable)
______________________________________________________________________________
User rules sign displayed  (choose one)
☐ OK     ☐ Defect     ☐ Not applicable
What is wrong?  (if applicable)
______________________________________________________________________________
Done at this visit  (tick all that apply)
☐ Water line cleaned
☐ Drained, cleaned and refilled
☐ Filter cartridge cleaned or replaced
☐ Pipework and jets inspected
☐ Flexible hoses disinfected
☐ Input air filter cleaned
Photos of defects  (photos: attach, or note the file names)
______________________________________________________________________________
Walk Cam: hot tub and spa pool check
Walk Cam video walk-through: available in the SiteSurvey app only.
4. Actions and sign-off
Result *  (choose one)
☐ Open for use     ☐ Closed until corrected
Why closed  (if applicable)
______________________________________________________________________________
Are further actions needed?
☐ Yes     ☐ No
Further actions  (copy this block for each one; if applicable)
What needs doing? *
______________________________________________________________________________
______________________________________________________________________________
______________________________________________________________________________
Who will do it?
______________________________________________________________________________
Due date
______________________________________________________________________________
Status  (choose one)
☐ Open     ☐ In progress     ☐ Completed
Inspector name *
______________________________________________________________________________
Position or company
______________________________________________________________________________
Inspector signature
	



	Signing records what was found on the day. It does not make unsafe equipment safe or replace a thorough examination, design check or service by a competent person.



Hot Tub and Spa Pool Check. Printable copy from the SiteSurvey form library. Fill it in on a phone, with photos and signatures: sitesurvey.app/forms/hot-tub-inspection-checklist/




