Hot Tub and Spa Pool Check

A hot tub and spa pool check to HSE HSG282: water clarity, pH and disinfectant tests with HSG282 action limits, jets, overflows, grilles and filter, cover, steps and cabinet, cleaning done, open or closed, and sign-off.

1. Hot tub

Project

______________________________________________________________________________

Client

______________________________________________________________________________

Site *

______________________________________________________________________________

Site address

______________________________________________________________________________

Check date *

______________________________________________________________________________

Time

______________________________________________________________________________

Checked by *

______________________________________________________________________________

Hot tub or spa pool (unit or location) *

______________________________________________________________________________

Setting  (choose one)

☐ Holiday park or lodge

☐ Hotel room

☐ Hotel or leisure spa

☐ Gym or club

☐ Showroom or display

☐ Other

Type  (choose one)

☐ Domestic-type hot tub     ☐ Commercial-type spa pool

Check  (choose one)

☐ Routine water test

☐ Between lettings (drain, clean and refill)

☐ Weekly check

☐ Monthly check

State  (choose one)

☐ In use     ☐ Not in use

Is the written control scheme (normal operating plan) on site?

☐ Yes     ☐ No

HSE HSG282 covers the control of legionella and other infectious agents in spa pools. Domestic-type hot tubs used as part of a business, for example in a holiday park rental unit or a hotel bedroom, are subject to the general duties of the Health and Safety at Work etc. Act 1974. HSG282 says records of monitoring, inspections, tests and checks should be kept for at least five years, and should show who did the work and when.

2. Water tests

HSG282 Table 1, domestic-type hot tubs: check water clarity, pH and disinfectant at least twice a day depending on the risk assessment and use; drain, clean the whole system and refill between each group of users or at least weekly, whichever is shorter. For commercial-type spa pools, test at opening and every two hours. Follow your own risk assessment.

Water tests  (copy this block for each one)

Time *

______________________________________________________________________________

Water clarity  (choose one)

☐ Clear     ☐ Cloudy

pH

______________________________________________________________________________

Disinfectant  (choose one)

☐ Chlorine     ☐ Bromine

Free chlorine or total active bromine (mg/l)

______________________________________________________________________________

Combined chlorine (mg/l)  (if applicable)

______________________________________________________________________________

If applicable: pH outside 7.0 to 7.6. HSG282 Table 3: close the spa pool and check the operation and calibration of the dosing units, then recheck.

If applicable: Disinfectant outside the HSG282 Table 3 limits (chlorine below 1 or above 10 mg/l, bromine below 2 or above 12 mg/l): close the spa pool, apply corrective actions and retest.

If applicable: Disinfectant outside the typical range (chlorine 3 to 5 mg/l, bromine 4 to 6 mg/l). HSG282 Table 3: check the dosing units are operating correctly.

If applicable: Combined chlorine above 1 mg/l. HSG282 Table 3: review the control measures.

Action taken  (if applicable; choose one)

☐ Closed until corrected     ☐ Corrected and retested

Dosing system working  (choose one)

☐ OK     ☐ Defect     ☐ Not fitted

Microbiological sample taken today?

☐ Yes     ☐ No

Sample reference and laboratory  (if applicable)

______________________________________________________________________________

If applicable: HSG282 Table 1 typical frequency: microbiological testing monthly (aerobic colony count, coliforms, E. coli, P. aeruginosa) and quarterly for legionella.

3. Condition

HSG282 says the review of a spa pool should include inspecting the accessible parts for damage and signs of contamination, such as biofilms, and the condition of the jets, overflows and grilles.

Water line clean  (choose one)

☐ OK     ☐ Defect     ☐ Not applicable

What is wrong?  (if applicable)

______________________________________________________________________________

Overflow channels and skimmer clean  (choose one)

☐ OK     ☐ Defect     ☐ Not applicable

What is wrong?  (if applicable)

______________________________________________________________________________

Jets: no damage, blockage or biofilm  (choose one)

☐ OK     ☐ Defect     ☐ Not applicable

What is wrong?  (if applicable)

______________________________________________________________________________

Suction grilles and strainers in place and undamaged  (choose one)

☐ OK     ☐ Defect     ☐ Not applicable

What is wrong?  (if applicable)

______________________________________________________________________________

Filter cartridge clean  (choose one)

☐ OK     ☐ Defect     ☐ Not applicable

What is wrong?  (if applicable)

______________________________________________________________________________

Cover, straps and locks secure  (choose one)

☐ OK     ☐ Defect     ☐ Not applicable

What is wrong?  (if applicable)

______________________________________________________________________________

Steps and surround: no damage or slip hazard  (choose one)

☐ OK     ☐ Defect     ☐ Not applicable

What is wrong?  (if applicable)

______________________________________________________________________________

Equipment cabinet closed and secure  (choose one)

☐ OK     ☐ Defect     ☐ Not applicable

What is wrong?  (if applicable)

______________________________________________________________________________

User rules sign displayed  (choose one)

☐ OK     ☐ Defect     ☐ Not applicable

What is wrong?  (if applicable)

______________________________________________________________________________

Done at this visit  (tick all that apply)

☐ Water line cleaned

☐ Drained, cleaned and refilled

☐ Filter cartridge cleaned or replaced

☐ Pipework and jets inspected

☐ Flexible hoses disinfected

☐ Input air filter cleaned

Photos of defects  (photos: attach, or note the file names)

______________________________________________________________________________

Walk Cam: hot tub and spa pool check

Walk Cam video walk-through: available in the SiteSurvey app only.

4. Actions and sign-off

Result *  (choose one)

☐ Open for use     ☐ Closed until corrected

Why closed  (if applicable)

______________________________________________________________________________

Are further actions needed?

☐ Yes     ☐ No

Further actions  (copy this block for each one; if applicable)

What needs doing? *

______________________________________________________________________________

______________________________________________________________________________

______________________________________________________________________________

Who will do it?

______________________________________________________________________________

Due date

______________________________________________________________________________

Status  (choose one)

☐ Open     ☐ In progress     ☐ Completed

Inspector name *

______________________________________________________________________________

Position or company

______________________________________________________________________________

Inspector signature

Signing records what was found on the day. It does not make unsafe equipment safe or replace a thorough examination, design check or service by a competent person.