Kitchen Extract Cleaning Record (TR19 Grease)
A kitchen extract cleaning record to TR19 Grease: usage band and frequency, canopy, filters, ductwork and fan, deposit thickness tests before and after, access panels, photos and the post-clean report.
1. System
Project
______________________________________________________________________________
Client
______________________________________________________________________________
Site *
______________________________________________________________________________
Site address
______________________________________________________________________________
Clean date *
______________________________________________________________________________
Time
______________________________________________________________________________
Technician *
______________________________________________________________________________
Company
______________________________________________________________________________
System and location (canopy reference and duct route) *
______________________________________________________________________________
Kitchen use *  (choose one)
☐ Heavy (12 to 16 hours a day)
☐ Moderate (6 to 12 hours a day)
☐ Light (2 to 6 hours a day)
	If applicable: TR19 Grease minimum: clean every 3 months.



	If applicable: TR19 Grease minimum: clean every 6 months.



	If applicable: TR19 Grease minimum: clean every 12 months.



Previous clean
______________________________________________________________________________
Days since the previous clean  (if applicable; worked out automatically in the app)
______________________________________________________________________________
	If applicable: The previous clean is after this clean date. Check both dates.



2. Clean
Cleaned *  (tick all that apply)
☐ Canopy     ☐ Filters     ☐ Plenum     ☐ Ductwork     ☐ Fan     ☐ Discharge
Access panels used
______________________________________________________________________________
Areas not cleaned and why
______________________________________________________________________________
Deposit thickness before (microns)
______________________________________________________________________________
Deposit thickness after (microns)
______________________________________________________________________________
	If applicable: TR19 Grease: grease deposits should not exceed a mean of 200 microns between cleans, and 500 microns or more needs immediate spot cleaning.



	If applicable: Over 200 microns before this clean. TR19 Grease limits the mean to 200 microns between cleans, so a shorter cleaning interval may be needed.



	TR19 Grease post-clean reports include before and after photos taken from matching positions.



Before photos  (photos: attach, or note the file names)
______________________________________________________________________________
After photos  (photos: attach, or note the file names)
______________________________________________________________________________
3. Post-clean report
Defects found (damaged ductwork, missing access panels, fire dampers)
______________________________________________________________________________
______________________________________________________________________________
______________________________________________________________________________
	BESA says many insurance policies require cleaning to TR19 Grease. The post-clean report includes a hygiene certificate with the date of the clean, the system location and the name of the competent technician.



Hygiene certificate or report reference
______________________________________________________________________________
Next clean due
______________________________________________________________________________
Site manager name
______________________________________________________________________________
Site manager signature
	



Completed by *
______________________________________________________________________________
Signature
	



Kitchen Extract Cleaning Record (TR19 Grease). Printable copy from the SiteSurvey form library. Fill it in on a phone, with photos and signatures: sitesurvey.app/forms/tr19-kitchen-extract-cleaning-record/




