Kitchen Extract Cleaning Record (TR19 Grease)

A kitchen extract cleaning record to TR19 Grease: usage band and frequency, canopy, filters, ductwork and fan, deposit thickness tests before and after, access panels, photos and the post-clean report.

1. System

Project

______________________________________________________________________________

Client

______________________________________________________________________________

Site *

______________________________________________________________________________

Site address

______________________________________________________________________________

Clean date *

______________________________________________________________________________

Time

______________________________________________________________________________

Technician *

______________________________________________________________________________

Company

______________________________________________________________________________

System and location (canopy reference and duct route) *

______________________________________________________________________________

Kitchen use *  (choose one)

☐ Heavy (12 to 16 hours a day)

☐ Moderate (6 to 12 hours a day)

☐ Light (2 to 6 hours a day)

If applicable: TR19 Grease minimum: clean every 3 months.

If applicable: TR19 Grease minimum: clean every 6 months.

If applicable: TR19 Grease minimum: clean every 12 months.

Previous clean

______________________________________________________________________________

Days since the previous clean  (if applicable; worked out automatically in the app)

______________________________________________________________________________

If applicable: The previous clean is after this clean date. Check both dates.

2. Clean

Cleaned *  (tick all that apply)

☐ Canopy     ☐ Filters     ☐ Plenum     ☐ Ductwork     ☐ Fan     ☐ Discharge

Access panels used

______________________________________________________________________________

Areas not cleaned and why

______________________________________________________________________________

Deposit thickness before (microns)

______________________________________________________________________________

Deposit thickness after (microns)

______________________________________________________________________________

If applicable: TR19 Grease: grease deposits should not exceed a mean of 200 microns between cleans, and 500 microns or more needs immediate spot cleaning.

If applicable: Over 200 microns before this clean. TR19 Grease limits the mean to 200 microns between cleans, so a shorter cleaning interval may be needed.

TR19 Grease post-clean reports include before and after photos taken from matching positions.

Before photos  (photos: attach, or note the file names)

______________________________________________________________________________

After photos  (photos: attach, or note the file names)

______________________________________________________________________________

3. Post-clean report

Defects found (damaged ductwork, missing access panels, fire dampers)

______________________________________________________________________________

______________________________________________________________________________

______________________________________________________________________________

BESA says many insurance policies require cleaning to TR19 Grease. The post-clean report includes a hygiene certificate with the date of the clean, the system location and the name of the competent technician.

Hygiene certificate or report reference

______________________________________________________________________________

Next clean due

______________________________________________________________________________

Site manager name

______________________________________________________________________________

Site manager signature

Completed by *

______________________________________________________________________________

Signature