Shower Head Descaling Record

A shower head and hose descaling record for legionella control: each outlet with its location, condition, descale and disinfection, temperatures and result, against the HSG274 quarterly frequency.

1. Visit

Project

______________________________________________________________________________

Client

______________________________________________________________________________

Site *

______________________________________________________________________________

Site address

______________________________________________________________________________

Date *

______________________________________________________________________________

Time

______________________________________________________________________________

Done by *

______________________________________________________________________________

Descaler and disinfectant used

______________________________________________________________________________

HSE HSG274 Part 2: dismantle, clean and descale removable parts, heads, inserts and hoses of showers and spray taps quarterly, or more often as the rate of fouling or other risk factors indicate, for example areas with high-risk patients.

2. Outlets

Showers and spray taps  (copy this block for each one)

Location *

______________________________________________________________________________

Scan the outlet tag

Scanned in the SiteSurvey app. On paper, write the numbers: asset number.

______________________________________________________________________________

Type  (choose one)

☐ Shower head and hose     ☐ Fixed shower head     ☐ Spray tap     ☐ Emergency shower

Scale or biofilm found  (choose one)

☐ None     ☐ Light     ☐ Heavy

Dismantled, cleaned and descaled?

☐ Yes     ☐ No

Head or hose replaced?

☐ Yes     ☐ No

Thermostatic mixing valve (TMV) fitted?

☐ Yes     ☐ No

Temperature at the outlet after 1 minute (°C)

______________________________________________________________________________

If applicable: Below 50 °C after one minute with no TMV. HSG274 says hot water should reach outlets at 50 °C (55 °C in healthcare premises) within one minute. Report it to the responsible person.

Result *  (choose one)

☐ Done     ☐ Not done: no access     ☐ Not done: defect

Notes  (if applicable)

______________________________________________________________________________

Photos (before and after)  (photos: attach, or note the file names)

______________________________________________________________________________

Outlets done  (worked out automatically in the app)

______________________________________________________________________________

Outlets with heavy scale  (worked out automatically in the app)

______________________________________________________________________________

If applicable: Heavy scale found. HSG274 allows a shorter interval than quarterly where the rate of fouling indicates it.

3. Sign-off

Next clean due

______________________________________________________________________________

Site contact name

______________________________________________________________________________

Site contact signature

Completed by *

______________________________________________________________________________

Signature