Shower Head Descaling Record
A shower head and hose descaling record for legionella control: each outlet with its location, condition, descale and disinfection, temperatures and result, against the HSG274 quarterly frequency.
1. Visit
Project
______________________________________________________________________________
Client
______________________________________________________________________________
Site *
______________________________________________________________________________
Site address
______________________________________________________________________________
Date *
______________________________________________________________________________
Time
______________________________________________________________________________
Done by *
______________________________________________________________________________
Descaler and disinfectant used
______________________________________________________________________________
	HSE HSG274 Part 2: dismantle, clean and descale removable parts, heads, inserts and hoses of showers and spray taps quarterly, or more often as the rate of fouling or other risk factors indicate, for example areas with high-risk patients.



2. Outlets
Showers and spray taps  (copy this block for each one)
Location *
______________________________________________________________________________
Scan the outlet tag
Scanned in the SiteSurvey app. On paper, write the numbers: asset number.
______________________________________________________________________________
Type  (choose one)
☐ Shower head and hose     ☐ Fixed shower head     ☐ Spray tap     ☐ Emergency shower
Scale or biofilm found  (choose one)
☐ None     ☐ Light     ☐ Heavy
Dismantled, cleaned and descaled?
☐ Yes     ☐ No
Head or hose replaced?
☐ Yes     ☐ No
Thermostatic mixing valve (TMV) fitted?
☐ Yes     ☐ No
Temperature at the outlet after 1 minute (°C)
______________________________________________________________________________
	If applicable: Below 50 °C after one minute with no TMV. HSG274 says hot water should reach outlets at 50 °C (55 °C in healthcare premises) within one minute. Report it to the responsible person.



Result *  (choose one)
☐ Done     ☐ Not done: no access     ☐ Not done: defect
Notes  (if applicable)
______________________________________________________________________________
Photos (before and after)  (photos: attach, or note the file names)
______________________________________________________________________________
Outlets done  (worked out automatically in the app)
______________________________________________________________________________
Outlets with heavy scale  (worked out automatically in the app)
______________________________________________________________________________
	If applicable: Heavy scale found. HSG274 allows a shorter interval than quarterly where the rate of fouling indicates it.



3. Sign-off
Next clean due
______________________________________________________________________________
Site contact name
______________________________________________________________________________
Site contact signature
	



Completed by *
______________________________________________________________________________
Signature
	



Shower Head Descaling Record. Printable copy from the SiteSurvey form library. Fill it in on a phone, with photos and signatures: sitesurvey.app/forms/shower-head-descaling-record/




