Smoke Vent and AOV Inspection

A smoke vent and AOV inspection: control panel and power, detector and switch activation, each vent opening fully and resetting, obstructions, faults and the reporting rules for high-rise residential buildings.

1. System

Project

______________________________________________________________________________

Client

______________________________________________________________________________

Site *

______________________________________________________________________________

Site address

______________________________________________________________________________

Test date *

______________________________________________________________________________

Time

______________________________________________________________________________

Engineer *

______________________________________________________________________________

System  (choose one)

☐ Natural smoke vents (AOVs)

☐ Mechanical smoke extract

☐ Smoke shaft

☐ Pressurisation system

Is it a residential building with two or more flats, at least 18 m high or with at least 7 storeys?

☐ Yes     ☐ No

If applicable: Regulation 7, Fire Safety (England) Regulations 2022: in high-rise residential buildings, smoke control systems and the fire detection linked to them are essential fire-fighting equipment. The responsible person must check them every month, record the checks and make the record available to residents, and report to the fire and rescue service by electronic means any fault not fixed within 24 hours, and again when it is fixed.

Article 17 of the Fire Safety Order: where needed to keep people safe, fire safety equipment and devices must be subject to a suitable system of maintenance and kept in an efficient state, in efficient working order and in good repair.

2. Controls

Control panel healthy, no faults showing  (choose one)

☐ OK     ☐ Defect

Battery backup tested  (choose one)

☐ OK     ☐ Defect

Activates from the smoke detector  (choose one)

☐ OK     ☐ Defect

Fire service override switch works  (choose one)

☐ OK     ☐ Defect     ☐ Not fitted

System resets and vents close afterwards  (choose one)

☐ OK     ☐ Defect

3. Vents

Vents  (copy this block for each one)

Location (stair head, corridor, lobby) *

______________________________________________________________________________

Type  (choose one)

☐ Window AOV     ☐ Roof vent     ☐ Damper     ☐ Fan

Opens fully  (choose one)

☐ OK     ☐ Defect

Time to open (seconds)

______________________________________________________________________________

Clear of obstructions  (choose one)

☐ OK     ☐ Defect

Actuator, chain and seals  (choose one)

☐ OK     ☐ Defect

What is wrong?  (if applicable)

______________________________________________________________________________

Photos  (photos: attach, or note the file names)

______________________________________________________________________________

Result *  (choose one)

☐ In efficient working order     ☐ Faults found

Faults and action  (if applicable)

______________________________________________________________________________

______________________________________________________________________________

______________________________________________________________________________

Who will fix the faults, and by when  (if applicable)

______________________________________________________________________________

Will the faults be fixed within 24 hours?  (if applicable)

☐ Yes     ☐ No

If applicable: Report the fault to the local fire and rescue service by electronic means as soon as reasonably practicable, and report again when it is fixed.

When and how the fire and rescue service was told  (if applicable)

______________________________________________________________________________

Completed by *

______________________________________________________________________________

Signature