Smoke Vent and AOV Inspection
A smoke vent and AOV inspection: control panel and power, detector and switch activation, each vent opening fully and resetting, obstructions, faults and the reporting rules for high-rise residential buildings.
1. System
Project
______________________________________________________________________________
Client
______________________________________________________________________________
Site *
______________________________________________________________________________
Site address
______________________________________________________________________________
Test date *
______________________________________________________________________________
Time
______________________________________________________________________________
Engineer *
______________________________________________________________________________
System  (choose one)
☐ Natural smoke vents (AOVs)
☐ Mechanical smoke extract
☐ Smoke shaft
☐ Pressurisation system
Is it a residential building with two or more flats, at least 18 m high or with at least 7 storeys?
☐ Yes     ☐ No
	If applicable: Regulation 7, Fire Safety (England) Regulations 2022: in high-rise residential buildings, smoke control systems and the fire detection linked to them are essential fire-fighting equipment. The responsible person must check them every month, record the checks and make the record available to residents, and report to the fire and rescue service by electronic means any fault not fixed within 24 hours, and again when it is fixed.



	Article 17 of the Fire Safety Order: where needed to keep people safe, fire safety equipment and devices must be subject to a suitable system of maintenance and kept in an efficient state, in efficient working order and in good repair.



2. Controls
Control panel healthy, no faults showing  (choose one)
☐ OK     ☐ Defect
Battery backup tested  (choose one)
☐ OK     ☐ Defect
Activates from the smoke detector  (choose one)
☐ OK     ☐ Defect
Fire service override switch works  (choose one)
☐ OK     ☐ Defect     ☐ Not fitted
System resets and vents close afterwards  (choose one)
☐ OK     ☐ Defect
3. Vents
Vents  (copy this block for each one)
Location (stair head, corridor, lobby) *
______________________________________________________________________________
Type  (choose one)
☐ Window AOV     ☐ Roof vent     ☐ Damper     ☐ Fan
Opens fully  (choose one)
☐ OK     ☐ Defect
Time to open (seconds)
______________________________________________________________________________
Clear of obstructions  (choose one)
☐ OK     ☐ Defect
Actuator, chain and seals  (choose one)
☐ OK     ☐ Defect
What is wrong?  (if applicable)
______________________________________________________________________________
Photos  (photos: attach, or note the file names)
______________________________________________________________________________
Result *  (choose one)
☐ In efficient working order     ☐ Faults found
Faults and action  (if applicable)
______________________________________________________________________________
______________________________________________________________________________
______________________________________________________________________________
Who will fix the faults, and by when  (if applicable)
______________________________________________________________________________
Will the faults be fixed within 24 hours?  (if applicable)
☐ Yes     ☐ No
	If applicable: Report the fault to the local fire and rescue service by electronic means as soon as reasonably practicable, and report again when it is fixed.



When and how the fire and rescue service was told  (if applicable)
______________________________________________________________________________
Completed by *
______________________________________________________________________________
Signature
	



Smoke Vent and AOV Inspection. Printable copy from the SiteSurvey form library. Fill it in on a phone, with photos and signatures: sitesurvey.app/forms/aov-inspection-checklist/




