Structured Cabling Test Record
A structured cabling test and handover record: cabling category, tester and calibration, permanent link or channel, links tested and passed, failures and retests, fibre results, labelling, drawings and warranty.
1. Installation
Project
______________________________________________________________________________
Client
______________________________________________________________________________
Site *
______________________________________________________________________________
Site address
______________________________________________________________________________
Test date *
______________________________________________________________________________
Time
______________________________________________________________________________
Installer *
______________________________________________________________________________
Cabling *  (choose one)
☐ Cat5e
☐ Cat6
☐ Cat6A
☐ Cat7 or Cat8
☐ Fibre OM3
☐ Fibre OM4
☐ Fibre OS2
☐ Mixed
Tester make and model
______________________________________________________________________________
Scan the tester label
Scanned in the SiteSurvey app. On paper, write the numbers: serial number.
______________________________________________________________________________
Tester calibration date
______________________________________________________________________________
Test configuration *  (choose one)
☐ Permanent link     ☐ Channel
	A permanent link is the permanently installed part of the cabling, from the connector at the patch panel to the outlet. A channel adds the patch cords and equipment cords at each end, so a channel result covers the cords that were in place when it was tested.



Test limit used (for example ISO/IEC or TIA Cat6A permanent link)
______________________________________________________________________________
2. Results
Copper links tested *
______________________________________________________________________________
Passed first time
______________________________________________________________________________
	If applicable: More links passed than were tested. Check the two numbers.



Pass rate (%)  (if applicable; worked out automatically in the app)
______________________________________________________________________________
Failures  (copy this block for each one)
Outlet or link ID *
______________________________________________________________________________
Fault  (choose one)
☐ Wire map     ☐ Length     ☐ NEXT     ☐ Return loss     ☐ Insertion loss     ☐ Other
Fix
______________________________________________________________________________
Retest  (choose one)
☐ Pass     ☐ Fail
Links still failing after retest  (worked out automatically in the app)
______________________________________________________________________________
Outstanding work: who will do it, and by when  (if applicable)
______________________________________________________________________________
Fibre cores tested
______________________________________________________________________________
Worst fibre loss (dB) and budget
______________________________________________________________________________
Tester reports or screenshots  (photos: attach, or note the file names)
______________________________________________________________________________
3. Handover
Handed over *  (tick all that apply)
☐ Full test results
☐ As-built drawings
☐ Labelling schedule
☐ Manufacturer warranty registration
☐ Rack and patching photos
Rack and patching photos  (photos: attach, or note the file names)
______________________________________________________________________________
	If a manufacturer's warranty is being registered, check which results it needs and who may submit them, and check the client's specification, before handover.



Client name
______________________________________________________________________________
Client signature
	



Completed by *
______________________________________________________________________________
Signature
	



Structured Cabling Test Record. Printable copy from the SiteSurvey form library. Fill it in on a phone, with photos and signatures: sitesurvey.app/forms/cable-test-report-template/




