TMV Service Record
A thermostatic mixing valve (TMV) service record: each valve with its location, outlet and type, set and measured mixed temperatures, fail-safe test, strainers and result, with a warning above 44°C.
1. Visit
Project
______________________________________________________________________________
Client
______________________________________________________________________________
Site *
______________________________________________________________________________
Site address
______________________________________________________________________________
Service date *
______________________________________________________________________________
Time
______________________________________________________________________________
Engineer *
______________________________________________________________________________
Thermometer and calibration date
______________________________________________________________________________
	HSE: where vulnerable people are at risk from scalding during whole-body immersion, water temperatures must not exceed 44°C. Where hot water is stored and distributed hot to control legionella, baths and showers should be fitted with TMVs, and outlet temperatures and TMVs should be monitored and maintained so the controls stay effective. HSE says TMVs need regular routine maintenance by competent people, in line with the manufacturer's instructions.



2. Valves
Valves  (copy this block for each one)
Location (room and outlet) *
______________________________________________________________________________
Scan the valve tag
Scanned in the SiteSurvey app. On paper, write the numbers: asset number, serial number.
______________________________________________________________________________
______________________________________________________________________________
Outlet  (choose one)
☐ Bath     ☐ Shower     ☐ Basin     ☐ Bidet     ☐ Sink     ☐ Other
Valve  (choose one)
☐ TMV2     ☐ TMV3     ☐ Other
Set mixed temperature (°C)
______________________________________________________________________________
Measured mixed temperature (°C) *
______________________________________________________________________________
	If applicable: Above 44°C. Reset or repair the valve before the outlet is used.



Fail-safe test (cold supply isolated)  (choose one)
☐ Pass     ☐ Fail
Strainers and check valves cleaned?
☐ Yes     ☐ No
Result *  (choose one)
☐ Pass     ☐ Fail
Action taken  (if applicable)
______________________________________________________________________________
______________________________________________________________________________
______________________________________________________________________________
Mixed temperature after adjustment (°C)  (if applicable)
______________________________________________________________________________
Valves failed  (worked out automatically in the app)
______________________________________________________________________________
Valves passed  (worked out automatically in the app)
______________________________________________________________________________
3. Actions and sign-off
Are further actions needed?
☐ Yes     ☐ No
Further actions  (copy this block for each one; if applicable)
What needs doing? *
______________________________________________________________________________
______________________________________________________________________________
______________________________________________________________________________
Who will do it?
______________________________________________________________________________
Due date
______________________________________________________________________________
Status  (choose one)
☐ Open     ☐ In progress     ☐ Completed
Inspector name *
______________________________________________________________________________
Position or company
______________________________________________________________________________
Inspector signature
	



	Signing records what was found on the day. It does not make unsafe equipment safe or replace a thorough examination, design check or service by a competent person.



TMV Service Record. Printable copy from the SiteSurvey form library. Fill it in on a phone, with photos and signatures: sitesurvey.app/forms/tmv-servicing-record/




